## CI major
Major Source Compression Ignition (CI) engines - diesel (and dual fuel if ≥ 2% diesel)
This document is intended solely as guidance, cannot be used to bind the Iowa Department of Natural Resources and is not a substitute for reading applicable statutes and regulations.
New or Existing | Commenced construction | Emergency or Non-emergency | HP | Requirements | Stack Testing | Monitoring | Recordkeeping | Reporting
Existing | before 12/19/2002 | Non-Emergency, not limited use (≥ 100 hr/yr) | > 500 HP | emission limit (70% CO reduction or 23 ppmvd CO), probably requires control; crankcase emission controls; ULSD | Every 3 years | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 12/19/2002 | Non-Emergency, limited use (< 100 hr/yr) | > 500 HP | none | N/A | N/A | hours of operation | N/A
Existing | before 6/12/2006 | Non-Emergency | 300 < HP ≤ 500 | emission limit (70% CO reduction or 49 ppmvd CO), probably requires control; crankcase emission controls; ULSD | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report (annual, if limited use)
Existing | before 6/12/2006 | Non-Emergency | 100 ≤ HP ≤ 300 | emission limit (230 ppmvd CO), should not require control | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report (annual, if limited use)
Existing | before 6/12/2006 | Non-Emergency | < 100 | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 12/19/2002 | Emergency, not used for DR | > 500 HP | None, if engine meets operating restrictions for emergency engines and is not used for DR | N/A | N/A | hours of operation | N/A
Existing | before 12/19/2002 | Emergency, used for DR | > 500 HP | Unclear whether maintenance requirements apply; ULSD (starting 1/1/15) | N/A | N/A | hours of operation | Annual operating hours report (first report due 3/31/16)
Existing | before 6/12/2006 | Emergency, not used for DR | ≤ 500 HP | maintenance requirements | N/A | N/A | maintenance; hours of operation | N/A
Existing | before 6/12/2006 | Emergency, used for DR | 100 < HP ≤ 500 | Maintenance requirements; ULSD (starting 1/1/15) | N/A | N/A | maintenance; hours of operation | Annual operating hours report (first report due 3/31/16)
Existing | before 6/12/2006 | Emergency, used for DR | ≤ 100 | maintenance requirements | N/A | N/A | maintenance; hours of operation | N/A
Existing |  | Black Start | all | maintenance requirements | N/A | N/A | maintenance | N/A
New | on or after 12/19/2002 | Non-Emergency, not limited use | > 500 HP | emission limit (70% CO reduction or 580 ppbvd formaldehyde), probably requires control; comply with NSPS 4I, if new enough | Every 6 months (note 1) | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
New | on or after 12/19/2002 | Non-Emergency, limited use | > 500 HP | comply with NSPS 4I, if new enough | N/A | N/A | hours of operation | initial notification
New | on or after 12/19/2002 | Emergency, not used for DR | > 500 HP | comply with NSPS 4I, if new enough | N/A | N/A | hours of operation | initial notification
New | on or after 12/19/2002 | Emergency, used for DR | > 500 HP | comply with NSPS 4I, if new enough; ULSD (starting 1/1/15) | N/A | N/A | hours of operation | initial notification; annual operating hours report (first report due 3/31/16)
New | on or after 6/12/2006 | All | ≤ 500 HP | comply with NSPS 4I | N/A | N/A | N/A | N/A
1. Semiannual testing can change to annual, after two tests show compliance.
2. All non-exempt engines are required to minimize idle time; startup time not to exceed 30 minutes.
3. For this summary, "used for DR" means an engine that operates or is contractually obligated to be available for more than 15 hours per calendar year for emergency demand response or voltage sag, or that operates at all for local reliability purposes.

## CI area
Area Source Compression Ignition (CI) engines - diesel (and dual fuel if ≥ 2% diesel)
This document is intended solely as guidance, cannot be used to bind the Iowa Department of Natural Resources and is not a substitute for reading applicable statutes and regulations.
New or Existing | Commenced construction | Emergency or Non-emergency | HP | Requirements | Stack Testing | Monitoring | Recordkeeping | Reporting
Existing | before 6/12/2006 | Non-Emergency, not limited use (≥ 100 hr/yr) | > 500 HP | emission limit (70% CO reduction or 23 ppmvd CO), probably requires control; crankcase emission controls; ULSD | Every 3 years | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, limited use (< 100 hr/yr) | > 500 HP | emission limit (70% CO reduction or 23 ppmvd CO), probably requires control; crankcase emission controls; ULSD | Every 5 years | control device parameters | maintenance, test results, hours of operation | initial notification, test reports, annual compliance report
Existing | before 6/12/2006 | Non-Emergency | 300 < HP ≤ 500 | emission limit (70% CO reduction or 49 ppmvd CO), probably requires control; crankcase emission controls; ULSD | One-time | N/A | maintenance | initial notification, test reports, semi-annual compliance report (annual, if limited use)
Existing | before 6/12/2006 | Non-Emergency | ≤ 300 | Maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 6/12/2006 | Emergency, not used for DR | all | Maintenance requirements | N/A | N/A | maintenance; hours of operation | N/A
Existing | before 6/12/2006 | Emergency, used for DR | > 100 HP | Maintenance requirements; ULSD (starting 1/1/15) | N/A | N/A | maintenance; hours of operation | Annual operating hours report (first report due 3/31/16)
Existing | before 6/12/2006 | Emergency, used for DR | ≤ 100 | Maintenance requirements | N/A | N/A | maintenance; hours of operation | N/A
Existing | before 6/12/2006 | Emergency, at a residential, institutional, or commercial facility; not used for DR | all | Exempt, if engine meets operating restrictions for emergency engines and is not used for DR | N/A | N/A | hours of operation | N/A
Existing | before 6/12/2006 | Black Start | all | Maintenance requirements | N/A | N/A | maintenance | N/A
New | on or after 6/12/2006 | all | all | comply with NSPS 4I | N/A | N/A | N/A | N/A
1. All non-exempt engines are required to minimize idle time; startup time not to exceed 30 minutes.
2. For this summary, "used for DR" means an engine that operates or is contractually obligated to be available for more than 15 hours per calendar year for emergency demand response or voltage sag, or that operates at all for local reliability purposes.

## SI major
Major Source Spark Ignition (SI) engines - gasoline, natural gas, LPG (and dual fuel if < 2% diesel)
This document is intended solely as guidance, cannot be used to bind the Iowa Department of Natural Resources and is not a substitute for reading applicable statutes and regulations.
New or Existing | Commenced construction | Emergency or Non-emergency | HP | Requirements | Stack Testing | Monitoring | Recordkeeping | Reporting
New or Existing |  | Non-Emergency, 4SRB | > 500 HP | emission limit (76% formaldehyde reduction or 350 ppbvd formaldehyde), probably requires control | One-time (note 4) | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 12/19/2002 | Any 2SLB or 4SLB | > 500 HP | None | N/A | N/A | N/A | N/A
Existing | before 6/12/2006 | Non-Emergency, 2SLB | 100 ≤ HP ≤ 500 | emission limit (225 ppmvd CO), should not require control | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, 4SLB | 100 ≤ HP ≤ 500 | emission limit (47 ppmvd CO), probably requires control | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, 4SRB | 100 ≤ HP ≤ 500 | emission limit (10.3 ppmvd formaldehyde), probably requires control | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, landfill/digester gas-fired | 100 ≤ HP ≤ 500 | emission limit (177 ppmvd CO) | One-time | N/A | maintenance, test results | initial notification, test reports, semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency | < 100 | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 12/19/2002 | Emergency, not used for DR | > 500 | None | N/A | N/A | hours of operation | N/A
Existing | before 12/19/2002 | Emergency, used for DR | > 500 | Unclear whether maintenance requirements apply | N/A | N/A | hours of operation | Annual operating hours report, starting with 2015
Existing | before 12/19/2002 | Limited use ( < 100 hr/yr) | > 500 | None | N/A | N/A | hours of operation | N/A
Existing | before 6/12/2006 | Emergency | ≤ 500 | maintenance requirements | N/A | N/A | maintenance, hours of operation | N/A
Existing |  | Black Start | all | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 12/19/2002 | Landfill/Digester gas > 10% of annual heat input | > 500 | None | N/A | N/A | N/A | N/A
New | on or after 6/12/2006 | 4SLB (manufactured before 1/1/08) | 250-500 HP | None | N/A | N/A | N/A | N/A
New | on or after 6/12/2006 | Non-emergency, 4SLB (manufactured after 1/1/08) | 250-500 HP | emission limit (93% CO reduction or 14 ppmvd formaldehyde), probably requires control | Every 6 months (note 1) | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
New | on or after 12/19/2002 | Non-Emergency, 4SLB | > 500 HP | emission limit (93% CO reduction or 14 ppmvd formaldehyde), probably requires control | Every 6 months (note 1) | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
New | on or after 12/19/2002 | Non-Emergency, 2SLB | > 500 HP | emission limit (58% CO reduction or 12 ppmvd formaldehyde), probably requires control | Every 6 months (note 1) | control device parameters | maintenance, test results | initial notification, test reports, semi-annual compliance report
New | on or after 6/12/2006 | 4SRB or 2SLB | ≤ 500 | comply with NSPS 4J, if new enough | N/A | N/A | N/A | N/A
New | on or after 6/12/2006 | 4SLB | < 250 | comply with NSPS 4J, if new enough | N/A | N/A | N/A | N/A
New | on or after 12/19/2002 | Emergency or limited use | > 500 | comply with NSPS 4J, if new enough | N/A | N/A | hours of operation | initial notification
New | on or after 6/12/2006 | Emergency or limited use | ≤ 500 | comply with NSPS 4J, if new enough | N/A | N/A | hours of operation | N/A
New | on or after 6/12/2006 | Landfill/Digester gas > 10% of annual heat input | ≤ 500 | comply with NSPS 4J, if new enough | N/A | N/A | N/A | N/A
New | on or after 12/19/2002 | Landfill/Digester gas > 10% of annual heat input | > 500 HP | separate fuel meters; comply with NSPS 4J, if new enough | N/A | N/A | daily fuel usage | initial notification; annual fuel usage report
1. Semiannual testing can change to annual, after two tests show compliance.
2. All non-exempt engines are required to minimize idle time; startup time not to exceed 30 minutes.
3. For this summary, "used for DR" means an engine that operates or is contractually obligated to be available for more than 15 hours per calendar year for emergency demand response or voltage sag, or that operates at all for local reliability purposes.
4. If > 5,000 HP complying with formaldehyde reduction, semi-annual testing.

## SI area
Area Source Spark Ignition (SI) engines - gasoline, natural gas, LPG (and dual fuel if < 2% diesel)
This document is intended solely as guidance, cannot be used to bind the Iowa Department of Natural Resources and is not a substitute for reading applicable statutes and regulations.
New or Existing | Commenced construction | Emergency or Non-emergency | HP | Requirements | Stack Testing | Monitoring | Recordkeeping | Reporting
Existing | before 6/12/2006 | Non-Emergency, 4SRB, not remote, operated > 24 hr/yr | > 500 HP | control with NSCR; no specific emission limit, but test result must demonstrate 75% CO reduction, 270 ppmvd CO, or 30% THC reduction | initial 3-run test; annual 1-run test; 15-minute runs okay for all tests | CPMS for catalyst inlet temp (Note 1) | maintenance, test results | Initial notification; test reports; semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, 4SLB, not remote, operated > 24 hr/yr | > 500 HP | control with oxidation catalyst; no specific emission limit, but test result must demonstrate 93% CO reduction or 47 ppmvd CO | initial 3-run test; annual 1-run test; 15-minute runs okay for all tests | CPMS for catalyst inlet temp (Note 1) | maintenance, test results | Initial notification; test reports; semi-annual compliance report
Existing | before 6/12/2006 | Non-Emergency, 4SRB or 4SLB, remote | > 500 HP | maintenance requirements | N/A | N/A | maintenance; justification for "remote" designation | N/A
Existing | before 6/12/2006 | Non-Emergency, 4SRB or 4SLB, operated 24 hr/yr or less | > 500 HP | maintenance requirements | N/A | N/A | maintenance, hours of operation | N/A
Existing | before 6/12/2006 | Non-Emergency, 2SLB | all | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 6/12/2006 | Non-Emergency, 4SRB or 4SLB | ≤ 500 | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 6/12/2006 | Black Start | all | maintenance requirements | N/A | N/A | maintenance | N/A
Existing | before 6/12/2006 | Emergency, not used for DR | all | maintenance requirements | N/A | N/A | maintenance, hours of operation | N/A
Existing | before 6/12/2006 | Emergency, used for DR | > 100 HP | maintenance requirements | N/A | N/A | maintenance, hours of operation | Annual operating hours report, starting with 2015
Existing | before 6/12/2006 | Emergency, used for DR | ≤ 100 | maintenance requirements | N/A | N/A | maintenance, hours of operation | N/A
Existing | before 6/12/2006 | Emergency, at a residential, institutional, or commercial facility; not used for DR | all | Exempt, if engine meets operating restrictions for emergency engines and is not used for DR | N/A | N/A | hours of operation | N/A
Existing | before 6/12/2006 | Non-Emergency, combusting landfill/digester gas > 10% annual heat input | all | maintenance requirements | N/A | N/A | maintenance | N/A
New | on or after 6/12/2006 | all | all | comply with NSPS 4J, if new enough | N/A | N/A | N/A | N/A
1. Or, equipment to shut down engine if catalyst inlet exceeds 1250 F.
2. All non-exempt engines are required to minimize idle time; startup time not to exceed 30 minutes.
3. For this summary, "used for DR" means an engine that operates or is contractually obligated to be available for more than 15 hours per calendar year for emergency demand response or voltage sag, or that operates at all for local reliability purposes.

## Sheet1
2014-07-14