## Aerated Lagoon Calcs
Lagoon Design Basis Loadings
30-d BOD5 | 170 | lbs/d
PE (0.17 lbs/capita/day) | 1000
ADW | 0.075 | MGD
AWW | 0.45 | MGD
18C | 0.1875 | MGD
Sludge Accumulation
Per capita sludge accumulation | 18.5 | gpcpy
Cell Volumes, Ice & Sludge Volumes, and Gross & Net 18C and AWW HRTs
Cell | Gross volume, MG | 18C Gross HRT, days | AWW Gross HRT, days | ADW Gross HRT, days | Ice Cover, MG | Sludge Volume, MG | Net Volume, MG | 18C Net HRT, days | AWW Net HRT, days | ADW Net HRT, days
1 | 2 | 10.6667 | 4.4444 | 26.6667 | 0.38 | 0.20386 | 1.4161 | 7.5528 | 3.147 | 18.8819
2 | 1.63 | 8.6933 | 3.6222 | 21.7333 | 0.32 | 0.16614 | 1.1439 | 6.1006 | 2.5419 | 15.2514
3 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
quiescent | 0.38 | 2.0267 | 0.84444 | 5.0667 |  |  | 0.38 | 2.0267 | 0.84444 | 5.0667
Totals | 4.01 | 21.3867 | 8.9111 | 53.4667 | 0.7 | 0.37 | 2.94 | 15.68 | 6.5333 | 39.2
Calculated BOD5 Removal Efficiencies (1st Order CSTR Model)
| AWW Conditions |  |  | ADW Conditions |  |  | 18C Design Flow Conditions
Influent BOD5 Conc., Co | 45.2678 | mg/L @ design loading and AWW |  | 271.6067 | mg/L @ design loading and ADW |  | 108.6427
Design Operating Temp., T | 1 | degrees C |  | 1 | degrees C |  | 1 | degrees C
K120 | 0.12 | reaction coefficient @ 20 degrees C |  | 0.12 | reaction coefficient @ 20 degrees C |  | 0.12 | reaction coefficient @ 20 degrees C
Temp. Correction Coeff. | 1.0372 |  |  | 1.0372 |  |  | 1.0372
K1design | 0.06 | reaction coefficient @ design temp. |  | 0.06 | reaction coefficient @ design temp. |  | 0.06 | reaction coefficient @ design temp.
Cell | Ce/Co | Ce (mg/L) | Ce (lbs/d) | Ce/Co | Ce (mg/L) | Ce (lbs/d) | Ce/Co | Ce (mg/L) | Ce (lbs/d)
1 | 0.69721 | 31.5612 | 118.526 | 0.27734 | 75.3269 | 47.1475 | 0.48965 | 53.1967 | 83.2402
2 | 0.74031 | 23.3651 | 87.7462 | 0.32209 | 24.2622 | 15.1859 | 0.54292 | 28.8818 | 45.1931
3 | 1 | 23.3651 | 87.7462 | 1 | 24.2622 | 15.1859 | 1 | 28.8818 | 45.1931
4 | 1 | 23.3651 | 87.7462 | 1 | 24.2622 | 15.1859 | 1 | 28.8818 | 45.1931
quiescent | 1 | 23.3651 | 87.7462 | 1 | 24.2622 | 15.1859 | 1 | 28.8818 | 45.1931
Note on D11: Bryant, Larry [DNR]: Based on 18C 1.54 days/100 mg/L SS, 0.2 lbs/cap/day, 100 gpcd -> 3.7 days or 370 gallons per capita over a 20-year period.
Note on H15: Bryant, Larry [DNR]: 12" average thickness at HWL.
Note on I15: Bryant, Larry [DNR]: Sludge distribution assumed proportional to aerated cell volume.

## SAGR Calcs
SAGR Design Influent
AWW Flow | 0.45 | MGD
30-d Max. BOD5 | 87.7462 | lbs/d
Max. Influent Conc. | 28.8818 | mg/L | OK
30-d Max. TKN | 36 | lbs/d
Loading Calcs (for 2-zone, 4-cell configuration)
Media Porosity | 0.4
Minimum Flux Area Required per Cell | 1754.9231 | sq. ft. | includes 75% flux reliability
Minimum Total HRT Volume Required | 75195.3125 | cu. ft.
Minimum Total TKN Volume Required | 90000 | cu. ft.
Minimum Total Volume Required | 90000 | cu. ft.